## Sheet1
No | Page | Question | Answer
1 | Page 12 of 66 Item 3 Scope of work | The service provider must install shelter with a lockable entrance gate…” is this in addition to the generator enclosure? | Yes, This is required for controlled access to the generator, and theft prevention.
2 |  | “The contractor must ensure that the phases are properly balanced”, which phases are these? The generator specified is single phase. | The generator is going to be connected to one (1) phase of the three (3) phases of the DB board. Therefore, the contractor must ensure that the phases are balanced without overloading other phases.
3 |  | “This installation must comply fully with all the sections and drawings of this document” – no drawings are included in the document – please forward these ASAP | The clause should actually read as follows: "The Contractor must provide a schematic drawing after installation"
4 | Page 13 of 66 Item 6 Detailed Specification: | The 15kVA generator specified is under rated to power the 10kVA UPS specified as well as the PC’s / plugs and number of lights to be connected to the generator, as detailed on page 16 of 66, Item 13, 2.1 Site Information, as well as the items specified under Item 7 on page 14 of 66. Do we quote as per the stipulated specifications, or for a generator with sufficient prime output on site to power the UPS as well as the items listed in 2.1, and Item 7? | The best approach is to quote for a generator with sufficient prime output on site to power the UPS as well as the items listed in 2.1 and Item 7. This is required for compliance purposes and to avoid straining the generator or the UPS.
5 | Page 13 of 66 Item 5.3.6 | please provide details of the “Re-wiring of Distribution Board” that you require carried out. | It is the responsibility of the contract to provide the GPAA with a schematic wiring diagram upon installation of the Generator and UPS. NB: Please ensure that all three phases are balanced on DB board.
6 |  | Is the Generator and UPS being installed inside a generator room or is it going to be outside? | The generator will be installed outside in the enclosed housing for that specific generator as mentioned in No. 1 above. The UPS will be installed inside the Server Room.
7 |  | Do we need to lay a Concrete Plinth or not? | Yes, refer to the Scope of Work (Page 5, point no.4)
8 |  | Can you please describe what you require under the item lockable shelter for generator storage ? | This is only a housing or enclosure to protect easy access to the generator, thus protecting it against theft.
9 |  | Is this the canopy for the generator ? | Yes, we use different descriptions for the same item.
10 |  | As per CIDBs advert it says the tender closes on 26 April 2016 and in your tender document it states 04 May 2016. Could you please confirm the correct closing date for the tender ? | The closing date is 4 May 2016 at 11h00
11 |  | At the site meeting they mentioned that diesel should be supplied. Is this for the commissioning and testing only or should the tanks be filled ? | The contractor shall supply sufficient diesel for testing and commissioning only , thereafter, re-fuelling shall be the responsibility of the GPAA.